## Utility Bills
Price per kWh ($) | Price per Peak kW ($) | Price per Therm ($) | Kwh Usage | Peak Kw Usage | Kwh Charge ($) | Peak Charge ($) | Total Electric Monthly Charges ($) | Gas Usage | Gas Charge ($) | Monthly Water Charges ($) | Monthly Sewer Charges ($)
0.08009 | 15.4426 |  | 604700 | 3273.8 | 48430.19 | 50556.11 | 99586.3 | 130320 | 233272.8 | 4198.29 | 1546.08

## VSD Replacement
Pre Loaded Cons(KW) | Pre Unloaded Cons(KW) | Pre Total Cons(KW) | Post Loaded Cons(KW) | Post Unloaded Cons(KW) | Post Total Cons(KW) | Peak KW Savings | Annual KWh Savings | Peak KW Cost Savings($) | Annual KWh Cost Savings($) | Total Savings($) | Capitol Cost($) | Labor Cost($) | Implementation Cost($) | SPP (Months)
150.2388 | 43.1537 | 193.3925 | 124.0083 | 18.6012 | 142.6096 | 50.7829 | 158442.7538 | 50.7829 | 158442.7538 | 13473.8416 | 45000 | 22500 | 67500 | 60.1165

## LED Replacement
Monthly Peak kW Reduction | Annual kWh Savings | Peak Cost Savings | kWh Cost Savings($) | Reduction Savings($) | Led Lifespan (years) | Replacement Cycles Bulbs (years) | Replacement Cycles Ballast (years) | Cost Avoidance total ($) | Annual Cost Avoidance ($) | Total Savings($) | Implementation Cost ($) | SPP months
59.5 | 371280 | 11026.0439 | 29735.6721 | 40761.716 | 8.0128 | 2.0833 | 1.25 | 81762.9167 | 10204.012 | 50965.728 | 155669 | 36.6526

## Pipe Insulation
Total Feet | # of Special Fittings | Total Labour Hours | Labor Cost | Insulation Cost | Special Covers Cost | Implementation Cost | SSP (years) | SPP (months) | ID | Description | Location | Diameter_inner_in | Length_ft | Surface_Temp | Q non | Q in | Q Diff | Non-Insulated | Insulated | Total Savings | Heat_Loss_Savings_Per_Hour | Peak_Demand_Reduction | Annual_Peak_Demand_Reduction | Annual_KWh_Reduction | Cost_Savings_Peak | Cost_Savings_KWh | Annual_Cost_Savings
85 | 7 | 10.2 | 934.63 | 810.05 | 931 | 2675.68 | 0.31 | 3.8 | 1 | Thin Pipe | 0559.mov | 2 | 14 | 253 | 4463.12 | 157.17 | 4305.95 | 44146.28 | 1660.01 | 42486 | 42486.26 | 12.45 | 149.42 | 77700.55 | 6223.01 | 2307.5 | 8530.51
[9 empty] | 2 | Thin Pipe | 0606.mov | 2 | 30 | 267 | 10295.48 | 362.56 | 9932.92
[9 empty] | 3 | Thick Pipe | 0606.mov | 4 | 3 | 267 | 2057.94 | 79.6 | 1978.34
[9 empty] | 4 | Flanges (Terminated) | 0604.mov | 4 | RIS | 443 | 1948.25 | 75.36 | 1872.89
[9 empty] | 5 | Valve + Flanges | 0604.mov | 2 | RIS | 254 | 480.8 | 16.93 | 463.87
[9 empty] | 6 | Boiler Pipe | 0604.mov | 2 | 8 | 120 | 696.82 | 24.54 | 672.28
[9 empty] | 8 | Boiler Line Pipe | Large Boiler | 3 | 30 | 270 | 15668.91 | 595.56 | 15073.35
[9 empty] | 9 | Flanges | Large Boiler | 6 | RIS | 288 | 8534.96 | 348.29 | 8186.66

## Air Leak Fix
W_comp | M_air | Power Loss | Kw Reduction | Total Kw Savings | Total Savings($) | Labor Cost ($) | Implementation Cost($) | SPP (months)
291.462 | 0.0027548 | 0.80293 | 16.0585 | 100205.3363 | 8273.3931 | 480 | 5480 | 7.9484