## Utility Bills
month | Kwh Usage | Peak Kw Usage | Kwh Charge ($) | Peak Charge ($) | Total Electric Monthly Charges ($) | Gas Usage | Gas Charge ($) | Monthly Water Charges ($) | Monthly Sewer Charges ($)
Jan-2023 | 41700 | 198.5 | 3769.41 | 2949.71 | 6769.12 | NA | NA | 288.49 | 114
Feb-2023 | 45800 | 228.5 | 4001.66 | 3395.51 | 7447.17 | NA | NA | 301.51 | 121.08
Mar-2023 | 65200 | 298.2 | 4886.55 | 4431.25 | 9367.8 | NA | NA | 333.26 | 131.1
Apr-2023 | 55900 | 297.9 | 3903.2 | 4426.79 | 8379.99 | NA | NA | 381.51 | 131.1
May-2023 | 49900 | 261.5 | 3720.8 | 3885.89 | 7656.69 | NA | NA | 341.92 | 131.1
Jun-2023 | 59800 | 277.3 | 4613.85 | 4384.11 | 9047.96 | NA | NA | 378.62 | 131.1
Jul-2023 | 47400 | 275.1 | 3849.89 | 4349.33 | 8249.22 | NA | NA | 414.91 | 131.1
Aug-2023 | 57200 | 274.4 | 4447.11 | 4338.26 | 8835.37 | NA | NA | 349.1 | 131.1
Sep-2023 | 52600 | 287.3 | 3992.8 | 4542.21 | 8585.01 | NA | NA | 547.25 | 131.1
Oct-2023 | 50400 | 312.7 | 3815.32 | 4950.04 | 8815.36 | NA | NA | 271.73 | 131.1
Nov-2023 | 39700 | 288.7 | 3715.47 | 4570.34 | 8335.81 | NA | NA | 299.06 | 131.1
Dec-2023 | 39100 | 273.7 | 3714.13 | 4332.67 | 8096.8 | NA | NA | 290.93 | 131.1

## Constants
Facility Variables Full | FC Var | FC Value | Units | Air Leak Variables Full | Air Leak Var | AL Values | Pipe Variables Full | Pipe Var | Pipe Values | LED Variables Full | LED Var | LED Value | VSD Variables Full | VSD Var | VSD Value
Factory Uptime (hours) | uptime_factory | 6240 |  | Compressor Efficiency | E_comp | 0.9 | Boiler Efficency | boiler_efficiency | 0.8 | Watts of current bulbs (Watts) | current_watts | 75 | Constat for Equation | const | 0.7456
Ambient Temp(F) | t_A | 70 |  | Loss Coefficient | C_dis | 0.61 | Method to Heat Pipe contents | type | Gas | Watts of LED bulbs (Watts) | led_watts | 45 | Cost of VSD compressor | vsd_cost | 45000
|  |  |  | Temperatur of line | T_line | 90 | R-Value of Air | r_Air | 0.3 | Total number of bulbs to replace | num_of_bulbs | 1700 | Cost of Installation | labor_cost | 22500
|  |  |  | Line Pressure (kPa) | P_line | 933 | K-Value of Insulation | k_insulation | 0.32 | Lifespan of LED bulb (hr) | led_hours | 50000
|  |  |  | Diameter of leak (m) | diameter_leak | 0.00135 | Thickness of insultion (in) | d_thickness | 2 | Lifespan of Fluorecent Bulbs (hr) | fluor_hours | 24000
|  |  |  | Number of Leaks | num_leaks | 20 | Length of Removable Insulation System (ft) | length_ris | 1.5 | Lifespan of Fluorecent Ballast (hr) | ballast_hours | 40000
|  |  |  | Time to fix Leaks | air_fix_time | 8 | Time to install one foot of insulation | pipe_manhour_conversion | 0.12 | Cost per fluorescent bulb ($) | fluor_cost | 9.24
|  |  |  | Number of Staff to fix | air_staff_needed | 2 | Labor Rate for Insulation | pipe_manhour_rate | 91.63 | Cost per ballast | ballast_cost | 11.96
|  |  |  | Isentopic constant for ideal Gas | n | 1.4 | Cost of one foot of insulation | pipe_mat_cost | 9.53 | Cost of labor per bulb | labor_cost | 6.67
|  |  |  | Specific Heat Ratio | K | 1.4 | Cost of one special fitting/RIS | pipe_sf_cost | 133 | Cost per LED fixture | led_fix_cost | 142
|  |  |  | Atmospheric Pressure (kPa) | P_atm | 101 |  |  |  | Cost per LED bulb | led_bulb_cost | 13.9
|  |  |  | Air Ideal gas constant (kj/kg*K) | R | 0.287
|  |  |  | Cost of Ultrasonic Leak Detector ($) | cost_ultrasonic | 5000
|  |  |  | Personnel Labor Rate ($) | labor_rate | 30

## Pipe Data
ID | Description | Amount_of_Fittings | Location | Material | Diameter_inner_in | Diameter_outer_in | Length_ft | Surface_Temp
1 | Thin Pipe | 1 | 0559.mov | Galvanized Steel | 2 | 2.375 | 14 | 253
2 | Thin Pipe | 1 | 0606.mov | Iron | 2 | 2.375 | 30 | 267
3 | Thick Pipe | 1 | 0606.mov | Iron | 4 | 4.5 | 3 | 267
4 | Flanges (Terminated) | 1 | 0604.mov | Iron | 4 | 4.5 | RIS | 443
5 | Valve + Flanges | 1 | 0604.mov | Iron | 2 | 2.375 | RIS | 254
6 | Boiler Pipe | 1 | 0604.mov | Iron | 2 | 2.375 | 8 | 120
8 | Boiler Line Pipe | 1 | Large Boiler | Iron | 3 | 3.5 | 30 | 270
9 | Flanges | 5 | Large Boiler | Iron | 6 | 6.625 | RIS | 288

## VSD Replacement
| Motor Hp | Motor Efficiency | Load Consumption | Unload Consumption
Pre | 200 | 93.3 | 94 | 27
Post | 200 | 96.2 | 80 | 12