## Bill Analysis
per_kwh_cost | per_kw_peak_cost
0.08009 | 15.4426

## Pipe Data
Total Feet | # of Special Fittings | Total Labour Hours | Labor Cost | Insulation Cost | Special Covers Cost | Implementation Cost | SSP (years) | SPP (months)
85 | 7 | 10.2 | 934.63 | 810.05 | 931 | 2675.68 | 0.31 | 3.8
ID | Description | Location | Diameter_inner_in | Length_ft | Surface_Temp | Q non | Q in | Q Diff
1 | Thin Pipe | 0559.mov | 2 | 14 | 253 | 4463.12 | 157.17 | 4305.95
2 | Thin Pipe | 0606.mov | 2 | 30 | 267 | 10295.48 | 362.56 | 9932.92
3 | Thick Pipe | 0606.mov | 4 | 3 | 267 | 2057.94 | 79.6 | 1978.34
4 | Flanges (Terminated) | 0604.mov | 4 | RIS | 443 | 1948.25 | 75.36 | 1872.89
5 | Valve + Flanges | 0604.mov | 2 | RIS | 254 | 480.8 | 16.93 | 463.87
6 | Boiler Pipe | 0604.mov | 2 | 8 | 120 | 696.82 | 24.54 | 672.28
8 | Boiler Line Pipe | Large Boiler | 3 | 30 | 270 | 15668.91 | 595.56 | 15073.35
9 | Flanges | Large Boiler | 6 | RIS | 288 | 8534.96 | 348.29 | 8186.66
Non-Insulated | Insulated | Total Savings
44146.28 | 1660.01 | 42486